SPILL PREVENTION AND RESPONSE PLAN

MEADOWBANK PRECIOUS METAL PROPERTY

NUNAVUT, CANADA

Prepared for:

5530 Nunavut Inc.

Prepared by:

Effective Date: June 1, 2017

Contents

1	Introduction	1

1.1	Contact Details	1

1.2	Purpose and Scope	1

1.3	Environmental Policy	1

1.4	Applicable Legislation and Guidelines	2

1.4.1	Federal	2

1.4.2	Territorial	3

1.5	Other Plans	3

1.6	Property and Camp Description	3

1.7	Hazardous Materials On-Site	4

1.8	Preventative Measures	4

2	Response Organization	5

2.1	Basic Steps	5

2.2	Chain of Command	6

3	Action Plan	6

3.1	Potential Spill Hazards	6

3.2	Potential Environmental Impacts	7

3.3	Initial Actions	7

3.4	Secondary Actions	8

3.5	Containment Procedures	8

3.5.1	Diesel, Jet Fuel, Gasoline, Hydraulic Oil and Lubricating Oil	8

3.5.1.1	Containment of Spills on Land	8

3.5.1.2	Containment of Spills of Water	9

3.5.1.3	Containment of Spills on Ice	9

3.5.1.4	Containment of Spills on Snow	10

3.5.1.5	Storage, Transfer and Disposal	10

3.5.2	Propane	11

3.5.2.1	Containment of Spills on Land	11

3.5.2.2	Containment of Spills on Water	11

3.5.2.3	Containment of Spills on Ice	11

3.5.2.4	Containment of Spills on Snow	11

3.5.2.5	Storage, Transfer and Disposal	11

3.5.3	Chemical Spills	11

4	Resource Inventory	12

4.1	On-site Resources	12

5	Training Program	13

5.1	On-site Personnel	13

5.2	Contractors	13

Tables

Table 1.1: Inventory of Hazardous Materials to be Stored on Site	4

Table 2.1: Spill Reporting and Response Contact List	6

Appendices

Appendix 1: Figures	14

Appendix 2: MSDS	16

Appendix 3: Daily Fuel Inspection Record	119

Appendix 4: NT-NU Spill Report Form	121

# Introduction

This Spill Prevention and Response Plan (“SPRP”) applies to mineral exploration activities conducted by 5530 Nunavut Inc. (the “Company”) on the Meadowbank Precious Metal Property (the “Property”), Nunavut, Canada.

This SPRP will come into effect June 1, 2017, pending approval. Copies and updates to this plan may be obtained via the Company or APEX Geoscience Ltd. (“APEX”).

## Contact Details

| 5530 Nunavut Inc. | APEX Geoscience Ltd. |
| --- | --- |
| 2205-1211 Melville Street | 110-8429-24 Street NW |
| Vancouver, BC V6E 0A7 | Edmonton, AB T6P 1L3 |
| Tel: (778) 389-7274 | Tel: (780) 467-3532 |
|  | Fax: (780) 467-4025 www.apexgeoscience.com |

## Purpose and Scope

The SPRP provides straightforward procedures for the storage and handling of fuels and other hazardous materials for the purpose of reducing the risk of environmental contamination and to ensure the health and safety of all personnel from the accidental release of deleterious materials. If an accidental release should occur, the SPRP provides clear response procedures. The goals of the Spill Prevention and Response Plan are to:

Promote safe handling and use of potentially hazardous materials;

Promote effective and safe recovery of spilled, potentially hazardous materials;

Reduce environmental impacts of spills to water and land;

Identify responsibilities and reporting procedures for spill events;

Provide site specific information about the facilities and contingencies in place;

Provide readily accessible emergency information to clean-up crews, management, and government agencies;

Comply with federal and territorial government regulations and guidelines pertaining to the preparation of a Spill Prevention and Response Plan and notification requirements in the event of a spill.

## Environmental Policy

5530 Nunavut Inc. is firmly committed to the protection and conservation of the natural environment, and to ensuring the health and safety of all employees, contractors, and people in surrounding communities. The environmental policy for the Meadowbank Precious Metal Property is to:

Develop the project in a socially and environmentally responsible manner;

Fully comply with all applicable environmental legislation and regulations;

Work in cooperation with federal, territorial, and local governments, as well as other relevant regulatory bodies, and the general public, on all aspects of environmental protection and policy;

Assess and mitigate any potential environmental impacts and minimize risks to the health and safety of all employees, contractors, and the general public;

Ensure contractors operate according to the Meadowbank Precious Metal Property environmental policies and procedures;

Employ an emergency response plan to reduce impacts of unforeseen events;

Provide ongoing instruction on Meadowbank Precious Metal Property environmental policies and spill prevention and response plans for all employees and contractors;

Keep employees, contractors, inspectors, government, and regulatory bodies informed of any changes at the site or with project activities.

For further detail regarding environmental policy, please refer to the Meadowbank Precious Metal Property “Environmental Management Plan”.

## Applicable Legislation and Guidelines

Acts, regulations, and legislation that relate to Environmental Management and Spill Prevention and Response in Nunavut are listed below:

### Federal

•	Canadian Environmental Protection Act

- Environment Canada's Environmental Emergency (E2) Regulations

- Implementation Guidelines for the Environmental Emergency Regulations

- Canadian Standards Association (CSA) Z1600-14 - Emergency and continuity management program

- National Oil Spill Preparedness and Response Regime

- National Energy Board requirements such as those in the Canada Oil and Gas Operations Act and Regulations and the Onshore Pipeline Regulations, 1999

- Environment Canada's Storage Tank Systems for Petroleum Products and Allied Petroleum Products Regulations

- Environment Canada's Guidelines for the Preparation of Hazardous Material Spill Contingency Plans, 1990

•	Fisheries Act

- Migratory Birds Convention Act

•	Nunavut Waters and Nunavut Surface Rights Tribunal Act

•	Transportation of Dangerous Goods Act

- Transportation of Dangerous Good Regulations

•	National Fire Code of Canada

•	Northern Land Use Guidelines

•	Workplace Hazardous Materials Information System (WHMIS)

•	CCME Environmental Codes of Practice for Aboveground and Underground Storage Tank Systems Containing Petroleum and Allied Petroleum Products

•	Storage Tank Systems for Petroleum Products and Allied Petroleum Products Regulations

•	Guidelines for Spill Contingency Planning (AANDC)

### Territorial

•	Northwest Territories and Nunavut Spill Contingency Planning and Reporting Regulations

- Contingency Planning and Spill Reporting In Nunavut – A guide to the New Regulations

- Guideline for Industrial Waste Discharges in Nunavut

- Fire Prevention Act

•	Environmental Protection Act

•	Mine Health and Safety Act and Regulations

•	Public Health Act

•	Safety Act

•	Nunavut Occupational Health and Safety Regulations

•	Environmental Guideline for the General Management of Hazardous Waste

## Other Plans

The SPRP should be considered as a part of the Property wide management system. Other management plans in place at the Meadowbank Precious Metal Property include:

Abandonment and Restoration Plan (ARP)

Emergency Response Plan (ERP)

Environmental Management Plan (EMP)

Fuel Management Plan (FMP)

Waste Management Plan (WMP)

## Property and Camp Description

The Meadowbank Precious Metal Property is located in the Kivalliq Region of Nunavut, within the 1:250,000 scale NTS map sheets, 66A and 66H. The Property is approximately 30 to 100 km north of the community of Baker Lake. The Property consists of three project areas: Area A to the north, Area B in the centre and Area C to the south (Figure 1 in Appendix 1).

The proposed exploration program will be supported by a temporary, 6 to 10 person exploration camp. The program is anticipated to commence June 15th, 2017 and run for 6 weeks (42 days). INAC, NWB and NIRB will be notified 30 days prior to the establishment of the camp and fuel cache. Personnel and cargo will be transported to the camp along the Agnico-Eagle Meadowbank Road and then flown to site via helicopter. Structures for the proposed camp may include 4 sleeper tents, 1 kitchen, 1 dry, 1 generator shack, and 1 outhouse. The majority of the structures will be insulated Weatherhaven tents, or similar, with tarp floors (Figure 2 in Appendix 1).

A fuel cache of less than 4,000 L (approximately 19 drums) will be established on stable ground near the camp, primarily to store diesel and jet fuel. Small quantities of gasoline and propane will also be stored. Small temporary fuel caches (less than 4,000 L), may also be required to supply the drilling and exploration programs. Within 30 days of the establishment of any temporary fuel cache, the appropriate agencies will be notified of the details of the cache including: GPS location, fuel type, container sizes, method of storage and proposed date of removal. The temporary fuel cache GPS locations will also be included in the annual reports submitted to the INAC, NWB and NIRB.

The proposed 2017 exploration activities for the Meadowbank Precious Metal Property include prospecting, till sampling and ground geophysical surveys. The intent of the 2017 exploration program is to delineate targets for diamond drilling. As soon as targets are identified for drilling INAC, NWB and NIRB will be notified and supplied with locations and maps. All exploration work and drilling will be strictly confined to the Areas A, B and C (Figure 1 in Appendix 1).

## Hazardous Materials On-Site

A main fuel cache will be established proximal to the camp, primarily to store diesel and jet fuel, with smaller quantities of gasoline and propane. Small fuel caches will also be established at drill sites while drilling is in progress. These temporary caches will store small amounts of diesel and propane, as needed for drilling. Other hazardous materials found on site may include small quantities of various lubricants/oil/grease for drilling and maintenance of motorized equipment, cleaning products, and waste oil.

Diesel, jet fuel, and gasoline will be stored in 205 litre (L) steel drums. Propane will be stored in 100 pound (lb) cylinders equipped with pressure relief valves. Waste oil will be sealed in 205 L steel drums and removed from camp for proper disposal.

Table 1.1: Inventory of Hazardous Materials to be Stored on Site

| Material | Container | Maximum in cache* |
| --- | --- | --- |
| Diesel | 205 L Drum | 8 Drums |
| Jet Fuel (Jet A or Jet B) | 205 L Drum | 10 Drums |
| Gasoline | 205 L Drum | 1 Drum |
| Propane | 100 lb Cylinder | 2 Cylinders |

- *Pending approval from AANDC, NWB and NIRB.

Further details on fuel storage and monitoring can be found in the Meadowbank Precious Metal Property “Fuel Management Plan”. Material Safety Data Sheets (MSDS) for each of the hazardous materials listed in Table 1.1 are included in Appendix 2.

## Preventative Measures

All fuels and other hazardous materials will be stored within “Arctic Insta-Berms”, or similar products, for secondary containment. These types of berms utilize chemical and fire resistant fabric (generally polyurethane coated nylon or vinyl coated polyester material) designed for extreme arctic temperatures and puncture resistance. “RainDrain” or similar hydrocarbon filtration systems will be used to safely remove any water collected inside the berms, and as a safeguard against any potential overflows of contaminated water.

Fuel drums will be stored on their sides in organized rows with the bungs in the three o’clock and nine o’clock positions. Drums will be stood upright 1 to 2 days prior to use in order to allow any contaminants to settle. Daily inspections will be conducted to identify any damaged or leaking containers, and the findings reported in the “Daily Fuel Inspection Record” (Appendix 3). In the event that a leak is discovered, the substance will either be used immediately or transferred to an undamaged container. Regular inspections and maintenance of motorized equipment will also be performed to avoid any fluid leaks onto the land. When possible, motorized equipment will be stored within berms.

Propane cylinders will be equipped with a pressure release valve that opens and closes to prevent a buildup of excessive internal pressure. Labels, showing data such as date of manufacture and re-testing dates, will be applied to the collar of the cylinders. Propane is non-toxic and will not contaminate soil, however secondary containment berms will be used for storage as a precaution. All propane cylinders will be secured for safety and stored away from any sources of ignition.

Electric or hand wobble pumps equipped with filtration devices will be used for the transfer of diesel, jet fuel, and gasoline from their storage containers directly to their end-use fuel tanks. Portable drip trays or mini-berms will be used to mitigate the risk of any spillage. Proper grounding procedures will always be used during fuel transfer while using an electric pump. Cigarette smoking, sparks, open flames, and any potential ignition sources are prohibited within 100 m of any fuel storage site and at all times during fuel transfer.

All chemical and fuel storage and fuel transfer areas will be located a minimum distance of 31 m from the normal high water mark of any water body. Spill kits and firefighting equipment will be strategically located near where any hazardous materials are stored or transferred, at all drill sites, in the helicopter(s), and at other locations throughout the camp. Section 4.1 provides details on spill kit contents.

Camp grey water from the kitchen and Dry will be a minimum of 31 m from the normal high water mark of any water body. The sump will maintain a minimum 1 metre (m) freeboard at all times. The sump and pipe will be inspected at regular intervals for leaks or overflow.

# Response Organization

In the case of a spill or environmental emergency, an immediate, safe and environmentally responsible reaction is required. All spills at the Meadowbank Precious Metal Property will be reported.

## Basic Steps

The basic steps of the response plan are as follows:

- Ensure the safety of all persons at all times.

- Identify and find the spilled substance and its source, and if possible, stop the process or shut off the source.

- Inform the on-site coordinator or his/her designate at once, so that immediate actions may be taken including notification of the 24 Hour Spill Report Line and an AANDC Water Resources Officer.

- Contain the spill or environmental hazard.

- Implement any necessary cleanup/remedial action.

## Chain of Command

- Immediately notify the 24 Hour Spill Report Line at 867-920-8130 (Fax: 867-873-6924), the AANDC in Nunavut at 1-800-567-9604, and Environment Canada at 867-975-4644.

- Before or after contacting the 24 Hour Spill Report Line, a Spill Report Form (Appendix 4) is to be filled out.

- Notify the project supervisor Rob L’Heureux (APEX) at 780-439-5380 or 780-916-5482.

Table 2.1: Spill Reporting and Response Contact List

| Contact | Telephone Number |
| --- | --- |
| 24 Hour Spill Report Line | 867-920-8130 |
| Rob L’Heureux, Project Supervisor (APEX Geoscience Ltd.) | 780-439-5380 (office) 780-916-5482 (mobile) |
| Fabio Capponi (5530 Nunavut Inc.) | (778) 389-7274 (mobile) |
| INAC (Nunavut) | 1-800-567-9604 |
| INAC Manager of Field Operations | (867) 975-4295 (Phone) (867) 979-6445 (Fax) |
| Environment Canada | 867-975-4644 24-hr page: 867-766-3737 |
| Government of Nunavut Department of Environment | 867-975-7700 (Iqaluit) |
| DFO (Central and Arctic Branch) | 519-383-1813 |
| Nunavut Water Board | 867-360-6338 |
| RCMP (Baker Lake) | 867-793-0123 |
| Baker Lake Health Centre | 867-793-2816 |
| Medevac (Yellowknife) | 867-873-5161 |
| CampSatellite Phone | TBA |
| Helicopter Satellite Phone | TBA |

* The Phone numbers for the satellite phone system used in camp and for the helicopter change annually. Once the numbers have been assigned, the SPRP will be updated.

# Action Plan

## Potential Spill Hazards

Even with appropriate precautions, the potential for spills remains when dealing with fuel and other hazardous materials. The following is a list of potential spill hazards:

205 L drums holding diesel, jet fuel, gasoline, waste fuels, and waste oils have the potential to leak or rupture due to mishandling. Older or refilled drums are more prone to leaking around the bungs if the seals are not properly maintained.

Propane cylinders may leak from the valves or rupture as a result of mishandling.

Vehicles and other motorized equipment may experience fuel or oil leaks as a result of malfunctions, impacts, lack of maintenance, improper storage, or faulty operation.

Leaks or spills may occur during fuel transfer due to over-fueling, improper fueling procedure, or faulty equipment.

The risk of rupturing a fuel container increases during transport due to the increased amount of handling involved.

Regular inspection and maintenance of fuel caches, motorized equipment, and fuel transfer equipment will help to mitigate the risks outlined above. Training for proper maintenance of motorized equipment, fuel transfer and handling procedures, and spill response training will be provided to applicable personnel.

## Potential Environmental Impacts

All hazardous materials pose a threat to the environment if spilled. Overall, spills in the winter are usually lower impact as snow is a natural sorbent and ice forms a barrier against soil or water contamination. The following list outlines potential environmental impacts of hazardous materials stored on site:

Gasoline may be harmful to wildlife and aquatic life. It is not readily biodegradable and has the potential for bioaccumulation in the environment. Gasoline volatizes quickly.

Diesel may be harmful to wildlife and aquatic life. It is not readily biodegradable and has the potential for bioaccumulation in the environment. Diesel burns slowly and thus the risk to the environment is reduced during recovery as it can be more readily contained compared to more volatile fuels.

Jet fuel may be harmful to wildlife and aquatic life. It is not readily biodegradable and has the potential for bioaccumulation in the environment. Jet fuel volatizes relatively quickly.

Propane may be harmful to wildlife and the surrounding environment, and it has the potential to accumulate in the environment. Propane is extremely volatile and is the most flammable material stored on site. Impacts to the immediate surrounding environment are of greatest concern.

Oils and greases may be harmful to wildlife and aquatic life. They are not readily biodegradable and have the potential for bioaccumulation in the environment.

Take action only if safety permits! NEVER SMOKE when dealing with spills!

## Initial Actions

Ensure safety of all personnel.

Assess spill hazards and risks.

Remove all sources of ignition.

Stop the spill if it is possible to do so safely.

Notify the supervisor and request assistance if needed.

Contain the spill.

## Secondary Actions

Determine the status of the spill event.

If necessary, pump fuel from a damaged or leaking tank or drum into a refuge container.

Notify the 24 Hour Spill Report Line.

Complete and fax a copy of the Spill Report Form (Appendix 4).

Notify permitting authorities.

If possible, resume cleanup and containment.

## Containment Procedures

Ensure it is safe to initiate containment procedures.

Always use applicable safety equipment (gloves, goggles/safety glasses, masks/respirators, etc.) before attempting to contain a spill.

Initiate spill containment by first determining what will be affected by the spill.

Assess speed and direction of the spill and the cause of movement (water, wind, slope).

Determine the best location for containing the spill, avoiding water bodies.

Have a contingency plan ready in case spill worsens beyond control or if other factors impede containment efforts.

### Diesel, Jet Fuel, Gasoline, Hydraulic Oil and Lubricating Oil

#### Containment of Spills on Land

Spills on land include spills on rock, gravel, soil and/or vegetation. It is important to note that soil is a natural sorbent, thus spills on soil are generally less serious than spills on water as contaminated soil can be more easily recovered. Generally spills on land occur during the late spring, summer or fall when snow cover is at a minimum. It is important that all measures be undertaken to avoid spills reaching open water bodies.

Dykes

Dykes can be created using soil surrounding a spill on land. These dykes are constructed around the perimeter or down slope of the spilled fuel. A dyke needs to be built up to a size that will ensure containment of the maximum quantity of fuel that may reach it. A plastic tarp can be placed on and at the base of the dyke such that fuel can pool up and subsequently be removed with sorbent materials or by pump into barrels or bags. If the spill is migrating very slowly a dyke may not be necessary and sorbents can be used to soak up fuels before they migrate away from the source of the spill.

Trenches

Trenches can be dug out to contain spills as long as the top layer of soil is thawed. Shovels pick axes or a loader can be used depending on the size of trench required. It is recommended that the trench be dug to the bedrock or permafrost, which will then provide containment layer for the spilled fuel. Fuel can then be recovered using a pump or sorbent materials.

#### Containment of Spills of Water

Spills on water such as rivers, streams or lakes are the most serious types of spills as they can negatively impact water quality and aquatic life. All measures need to be undertaken to contain spills on open water.

Booms

Booms are commonly used to recover fuel ﬂoating on the surface of lakes or slow moving streams. They are released from the shore of a water body to create a circle around the spill. If the spill is away from the shoreline a boat will need to be used to reach the spill, then the boom can be set out. More than one boom may be used at once. Booms may also be used in streams and should be set out at an angle to the current. Booms are designed to ﬂoat and have sorbent materials built into them to absorb fuels at the edge of the boom. Fuel contained within the circle of the boom will need to be recovered using sorbent materials or pumps and placed into barrels or bags for disposal.

Weirs

Weirs can be used to contain spills in streams and to prevent further migration downstream. Plywood or other materials found on site can be placed into and across the width of the stream, such that water may still ﬂow under the weir. Spilled fuel will ﬂoat on the water surface and be contained at the foot of the weir. It can then be removed using sorbents, booms or pumps and placed into barrels or plastic bags.

Barriers

In some situations barriers made of netting or fence material can be installed across a stream, and sorbent materials placed at the base to absorb spilled fuel. Sorbents will need to be replaced as soon as they are saturated. Water will be allowed to ﬂow through. This is very similar to the weir option discussed above.

Note that in some cases, it may be appropriate to burn fuel or to let volatile fuels such as gasoline evaporate after containment on the water surface. This should only be undertaken in consultation with, and after approval from the AANDC or lead agency Inspector.

#### Containment of Spills on Ice

Spills on ice are generally the easiest spills to contain due to the predominantly impermeable nature of the ice. For small spills, sorbent materials are used to soak up spilled fuel. Remaining contaminated ice/ slush can be scraped and shoveled into a plastic bag or barrel. However, all possible attempts should be made to prevent spills from entering ice covered waters as no easy method exists for containment and recovery of spills if they seep under ice.

Dykes

Dykes can be used to contain fuel spills on ice. By collecting surrounding snow, compacting it and mounding it to form a dyke down slope of the spill, a barrier is created thus helping to contain the spill. If the quantity of spill is fairly large, a plastic tarp can be placed over the dyke such that the spill pools at the base of the dyke. The collected fuel can then be pumped into barrels or collected with sorbent materials.

Trenches

For signiﬁcant spills on ice, trenches can be cut into the ice surrounding and/or down slope of the spill such that fuel is allowed to pool in the trench. It can then be removed via pump into barrels, collected with sorbent materials, or mixed with snow and shoveled into barrels or bags.

Burning

Burning should only be considered if other approaches are not feasible, and is only to be undertaken with the permission of the AANDC or lead agency Inspector.

#### Containment of Spills on Snow

Snow is a natural sorbent, thus as with spills on soil, spilled fuel can be more easily recovered. Generally, small spills on snow can be easily cleaned up by raking and shoveling the contaminated snow into plastic bags or empty barrels, and storing these at an approved location.

Dykes

Dykes can be used to contain fuel spills on snow. By compacting snow down slope from the spill, and mounding it to form a dyke, a barrier or berm is created thus helping to contain the spill. If the quantity of spill is fairly large, a plastic tarp can be placed over the dyke such that the spill pools at the base of the dyke. The collected fuel/snow mixture can then be shoveled into barrels or bags, or collected with sorbent materials.

#### Storage, Transfer and Disposal

In most cases, spill cleanups are initiated at the far end of the spill and contained moving toward the centre of the spill. Sorbent socks and pads are generally used for small spill clean-up. A pump with attached fuel transfer hose can suction spills from leaking containers or large accumulations on land or ice, and direct these larger quantities into empty drums. Hand tools such as cans, shovels, and rakes are also very effective for small spills or hard to reach areas. Heavy equipment can be used if deemed necessary, and given space and time constraints.

Used sorbent materials are to be immediately placed in plastic bags, and later in sealed containers for future disposal. All materials mentioned in this section are available in the spill kits located at camp, drill sites and fuel caches. Following clean up, any tools or equipment used will be properly washed and decontaminated, or replaced if this is not possible.

All contaminated soil, water, ice, snow, and supplies used for clean-up will be stored in sealed, labeled containers and removed from site for proper disposal at an approved facility. The movement of hazardous wastes will be monitored by the Nunavut Department of Environment and tracked with a Waste Manifest during all movements and transfers.

### Propane

It is not possible to contain vapors when released. Water spray can be used to knock down vapors if no chance of ignition exists. Personnel should leave the area immediately unless a small leak is stopped immediately following detection. Personnel should avoid touching release points on damaged containers as frost may form rapidly. If tanks are damaged, do not attempt a recovery – allow gas to disperse. Keep clear of tank ends. Small fires can be extinguished with a dry chemical CO2 fire extinguisher.

#### Containment of Spills on Land

Do not attempt to contain propane release.

#### Containment of Spills on Water

Do not attempt to contain propane release.

#### Containment of Spills on Ice

Do not attempt to contain propane release.

#### Containment of Spills on Snow

Do not attempt to contain propane release.

#### Storage, Transfer and Disposal

It is not possible to contain released vapors. Contaminated materials and damaged containers will be sent to an approved facility for disposal. The movement of hazardous wastes will be monitored by the Nunavut Department of Environment and tracked with a Waste Manifest during all movements and transfers.

### Chemical Spills

Assess hazard of spilled material; REFER TO MSDS. Members of the emergency response team who are vulnerable to certain contaminants should be replaced with alternatives (e.g. Asthmatics where fumes or airborne particles are evident).

Assemble applicable safety equipment (gloves, goggles/safety glasses, masks/respirators, etc.) before responding to a spill.

Apply absorbents to soak up liquids.

Solid chemicals such as dusts or powders should be covered with plastic sheeting to prevent disbursement by wind or animal.

Neutralize acids or caustics. Place spilled material and contaminated clean-up supplies in empty refuge drums and seal for disposal.

Contact the 24 Hour Spill Report Line.

Proceed with clean-up in correspondence with the MSDS and steps in section 3.

# Resource Inventory

Spill kits and firefighting equipment will be strategically located near where any hazardous materials are stored or transferred, at all fuel caches, drill sites, in the helicopter(s), and at numerous locations throughout the camp.

## On-site Resources

Spill kits will be in bright yellow 231 L rigid plastic containers and will contain:

100	oil sorbent pads

6	small pillows

2	large pillows

2	3”x4’ socks

5	3”x8’ socks

2	4’ socks

1        25 lb bag granular

2	pair splash goggles

2	poly coated Tyvek suits

2	disposable respirators

10	large bags with ties for temporary use

2	large tarps

1	collapsible shovel

1	roll duct tape

1	utility knife

2	spill kit labels

1	laminated copy of the Meadowbank Precious Metal Property Spill Prevention and Response Plan

1	231 L overpack drum

1	checklist of required items

Other equipment on-site:

2 	38”x144’ rolls absorbent matting

200	16”x20” enviro matting

10	booms

5	large tarps

5	shovels (minimum)

3	pick axes (minimum)

3	rakes (minimum)

10	empty 205 L drums (minimum)

Spill kits will be located:

Camp fuel cache

Helicopter pad / air strip

Drill fuel caches

Generator shack

Incinerator

Additional spill kits around camp

# Training Program

## On-site Personnel

All on-site personnel will undergo an orientation and training program on initial spill response procedures and be familiar with spill reporting requirements. Fuel handling personnel will receive additional training in safe operation of fuel transfer equipment, spill prevention techniques and spill response. The on-site project supervisor will keep detailed training records.

A designated Emergency Response Team (ERT) made up of on-site personnel will be established. Members of the ERT will receive comprehensive and ongoing training in emergency spill response. ERT members will be on-site at all times and will be made aware of the available resources and locations of spill kits.

Training will include, but not be limited, to the following:

Review of the SPRP and ERT member responsibilities.

Location of fuel and chemical storage sites.

Causes and possible effects of spills.

Use of on and off-site spill response resources.

Exercises in spill response and spill kit use.

Distribution of up-to-date copies of the SPRP and emergency contact lists.

All on-site personnel are required to have basic training in first aid, WHMIS, and Transportation of Dangerous Goods (TDG). Supervisors are required to have advanced first aid training, as well as a valid Occupational Health and Safety (OHS) Supervisor’s Certificate.

## Contractors

All contractors will complete site-specific health and safety training including, but not limited to: WHMIS, TDG, and OSH training.

Appendix 1: Figures

Appendix 2: MSDS

Appendix 3: Daily Fuel Inspection Record

Appendix 4: NT-NU Spill Report Form