APPENDIX – FUEL STORAGE AND CONTAINMENT DESCRIPTION

1.0 PURPOSE

This appendix provides a detailed description of fuel storage, secondary containment, handling, and site management measures associated with the 2026 diamond drilling program at the Esker Gold Project.

The objectives are to:

• Prevent fuel releases to land, surface water, and groundwater;
• Quantify maximum onsite fuel volumes;
• Demonstrate compliance with applicable territorial requirements and land use approvals;
• Confirm that fuel storage will not result in permanent land disturbance.

2.0 FUEL TYPES AND MAXIMUM ONSITE QUANTITIES

2.1 Fuel Types

The following petroleum products may be present during the 2026 field season:

• Diesel fuel (primary fuel for drill, generators, pumps)
• Gasoline (small equipment use)
• Propane (camp cooking/heating)
• Lubricants and hydraulic fluids (small quantities)

2.2 Maximum Onsite Volumes (At Any Given Time)

| Product | Maximum Onsite Volume | Storage Method | Notes |
| --- | --- | --- | --- |
| Diesel | 2,500–4,000 L | 210 L drums and/or approved portable tanks | Primary fuel source |
| Gasoline | <500 L (estimated) | CSA-approved containers | Small equipment only |
| Propane | Standard cylinders | Upright secured cylinders | Camp use |
| Lubricants / Oils | <200 L combined | Original sealed containers | Maintenance use |

Estimated total seasonal diesel consumption: approximately 40,000 L.
Maximum onsite volume represents storage capacity at one time and not cumulative seasonal throughput.

3.0 FUEL STORAGE LOCATION AND LAND USE CONTROLS

• Fuel storage areas will be located a minimum of 100 metres from lakes, streams, and drainage channels where practicable;
• Storage will be positioned on stable, relatively level terrain;
• No vegetation clearing beyond minimal leveling will be required;
• No roads or permanent access corridors will be constructed;
• Storage footprint estimated at approximately 5 m × 5 m (25 m²) per storage location.

Fuel storage areas are temporary and will be fully removed at season end.

4.0 SECONDARY CONTAINMENT DESIGN

All bulk diesel storage will utilize secondary containment designed to provide a minimum capacity of 110% of the largest container.

4.1 Example Containment Calculation

If a 1,000 L tank is used:

Required containment capacity = 1,000 L × 110% = 1,100 L minimum.

If 210 L drums are used:

Largest container = 210 L
Required containment capacity = 231 L minimum.

Containment systems will consist of:

• Impermeable liner (synthetic or equivalent);
• Bermed perimeter or rigid containment frame;
• Stable base to prevent puncture or settlement;
• Protection from precipitation accumulation (inspection and pump-out if required).

5.0 FUEL HANDLING AND TRANSFER PROCEDURES

• Refueling conducted by trained personnel only;
• Pumps attended at all times;
• Spill trays used at hose connections;
• No refueling within 100 m of water unless fully contained;
• Immediate shutdown of transfer operations if leak observed.

Helicopter-Supported Operations

• No refueling over open water;
• Fuel sling loads minimized and not flown over water where practicable;
• Spill kit present at helicopter refueling location;
• Damaged drums removed from service immediately.

6.0 INSPECTION, MONITORING, AND RECORD KEEPING

• Daily inspection of fuel storage and containment areas;
• Inspection of drum integrity, tank valves, hoses, and liner condition;
• Fuel inventory log maintained;
• Any observed leakage addressed immediately.

Fuel management is overseen by a designated Fuel / Environmental Monitor.

7.0 SPILL RESPONSE INTEGRATION

Fuel storage controls are integrated with the Project Spill Contingency Plan.

In the event of a spill:

• Source will be stopped immediately;
• Spill will be contained using absorbent materials;
• Contaminated soil will be excavated if required;
• Reportable spills will be communicated to the Nunavut Spill Line and relevant authorities;
• Contaminated materials will be removed from site for approved disposal.

No contaminated material will be buried without regulatory direction.

8.0 DEMOBILIZATION AND SITE RESTORATION

At the conclusion of the 2026 drilling season:

• All drums, tanks, and containment liners will be removed;
• Berms dismantled and area graded;
• Area inspected for contamination;
• Any impacted soils remediated;
• Site stabilized to blend with surrounding terrain.

No permanent fuel storage infrastructure will remain onsite.

9.0 SUMMARY TABLE – FUEL STORAGE AND ENVIRONMENTAL PROTECTION

| Component | Design Control | Environmental Protection Function |
| --- | --- | --- |
| Diesel Storage | Secondary containment ≥110% | Prevents soil/water contamination |
| Setbacks | ≥100 m from water (where practicable) | Reduces spill migration risk |
| Storage Footprint | ~25 m² per location | Temporary disturbance only |
| Drum/Tank Inspection | Daily checks | Early leak detection |
| Refueling Controls | Attended transfer, spill trays | Prevents accidental releases |
| Demobilization | Full removal of systems | No long-term disturbance |